COMMONWEALTH of VIRGINIA

Department of Health

Karen Shelton, MD	P O BOX 2448	TTY 7-1-1 OR

State Health Commissioner	RICHMOND, VA 23218	1-800-828-1120

R. Christopher Lindsay

Chief Operating Officer

July 1, 2024

Mr. Samuel C Hampsher-Monk

compliance@vpcglobal.com

VPCglobal.com

Dear Mr. Hampsher-Monk,

On May 16, 2024 you submitted documentation on the following septic tanks for approval by the Virginia Department of Health, Office of Environmental Health, Division of Water and Wastewater Services.

| Model Number | Description |
| --- | --- |
| 87-41718 | 1000 Gallon Single Compartment Septic Tank Yellow |
| 87-41720 | 1000 Gallon Two Compartment Septic Tank Yellow |
| 87-41758 | 1500 Gallon Single Compartment Septic Tank Yellow |
| 87-41760 | 1500 Gallon Two Compartment Septic Tank Yellow |

The subject tanks do not meet the following Sewage Handling and Disposal Regulations (12VAC5-610-815) criteria:

1-2 inch difference between inverts of inlet and outlet structures (3 inches provided)

However, after reviewing the information provided by VPC global, the Office of Environmental Health Services approves the tank for use in Virginia when used with an NSF-certified effluent filter.

Sincerely,

Lance Gregory

Director

Division of Onsite Water and Wastewater Services